## Zone 1
General Data | 1.0 | Customer Data
| 1.1 | Data Sheet No.
| 1.2 | Location: | ISRAEL
| 1.3 | Plant/Unit: | ASHKELON
| 1.4 | Project Name:
| 1.5 | Motor Function: | Concentrate Pump for Firefighting
| 1.6 | Motor Tag Number | FP - 0004
| 1.7 | Max./Min. Ambient. Temp.: | 0-400C
| 1.8 | Altitude Over Sea Level | 10m.
| 1.9 | Relative Humidity: | 90%
| 1.10 | Atmosphere: | Petrochemicals
| 1.11 | Enviroment classification | Non Hazardous Locations
| 1.12 | Type: | TEFC/IP-55
| 1.13 |  | GENERAL
| 1.14 | Specification: | I.E.C
| 1.15 | Prepared By: | A.S.
| 1.16 | Date: | 2022-06-08
| 2.0 | Customer Motor Requirements
Electrical Data | 2.1 | Motor Type: | Cage Rotor
| 2.2 | Rated Output | 50 | HP
| 2.3 | Rated Voltage: | 400 | V
| 2.4 | Phases: | 3
| 2.5 | Frequency: | 50 | Hz
| 2.6 | Stator Winding Connection: | Y/Δ
| 2.7 | Number Of Terminals: | 6 - On terminal plate
| 2.8 | Starting Method: | D.O.L.
| 2.9 | Insulating Class: | F
| 2.10 | Stator Wind. Max. Temp.class | B
| 2.11 | Efficiency Class | EFF-3/PREMIUM
| 2.12 | Thermal Protection Device Type | N/A
| 2.12.1 | Mounted in a separate terminal box | N/A
| 2.12.2 | Control Cable Entries – Number/Size | N/A
| 2.13 | No.of Thermal Protection Device in winding | N/A
| 2.14 | No.of Thermal Protection Device in bearings | N/A
| 2.15 | Anti Condensation Heater type | 1X99 W-230 VAC
| 2.15.1 | Mounted in a separate terminal box | YES
| 2.15.2 | Control Cable Entries – Number/Size | 1/M20
| 2.16 | Stating Freq. (No. Of Starts/1H from hot) : | 4
| 2.17 | Duty | S1
| 2.18 | Service Factor: | 1.15
| 2.19 | Synchronous Speed: | 1480 | r.p.m
Mechanical Data | 2.20 | Cable Size | 4X10 | mm2
| 2.21 | Cable Type | N2XY
| 2.22 | Enclosure Material: | CAST IRON
| 2.23 | Type Of Enclosure - Motor: | TEFC/IP-55
| 2.24 | Terminal Box Enclosure | IP-55
| 2.25 | Power Cable Entries – Number/size | 1 FOR CABLE ø 23 mm
| 2.26 | Power Terminal Box Location | N/A
|  | Control Terminal Boxes Location | N/A
| 2.27 | Paint Standard | Epoxy
| 2.28 | Frame Size: | VSS-T324/MONOBLOK
| 2.29 | Type Of Load: | HORIZONTAL PUMP
| 2.30 | Type Of Coupling: | N/A
|  | Bearing Type: | DE-7…, NDE-6…
| 2.31 | Bearing Lubrication Type: | Grease
| 2.32 | Mounting: | B3
| 2.33 | Canopy for vertical mounted motor | N/A
| 2.34 | Direction Of Rotation (Viewed From The Drive End) | BIDIRECTIONAL
| 2.35 | Vibration Category: | NORMAL
| 2.36 | Method of Cooling: | AIR
| 3.0 | Manufacturer Motor Data
General Data | 3.1 | Prepared By:
| 3.2 | Date:
| 3.3 | Manufacturer:
| 3.4 | Motor Type
| 3.5 | Frame Size:
| 3.6 | Enviroment classification
| 3.7 | Type:
3.8
| 3.9 | Rated Power |  | HP
Electrical Data | 3.10 | Full Load Current: |  | A
| 3.11 | Locked Rotor Current: |  | x In
| 3.12 | No Load Current: |  | A
| 3.13 | Power Factor At: 100% Full Load:
| 3.13.1 | 80% Full Load:
| 3.13.2 | 70% Full Load:
| 3.13.3 | 50% Full Load:
| 3.13.4 | No Load:
| 3.14 | Efficiency Class
| 3.14.1 | Efficiency At: 100% Full Load: |  | %
| 3.14.2 | 80% Full Load: |  | %
| 3.14.3 | 70% Full Load: |  | %
| 3.14.4 | 50% Full Load: |  | %
| 3.15 | Rated Torque: |  | Kg-m
| 3.16 | Locked Rotor Torque: |  | x Tn
| 3.17 | Breakdown Torque: |  | x Tn
Mechanical Data | 3.18 | Bearing Type On DE
| 3.19 | Bearing Type On NDE
| 3.20 | Method of Cooling:
| 3.21 | Max. Permis. Temp. Of Bearings
| 3.22 | Type Of Enclosure - Motor:
| 3.23 | Terminal Box Enclosure
| 3.24 | Net Weight: |  | Kg.
| 3.25 | Weight Of Rotating Parts: |  | Kg.
| 3.26 | Rotor Moment of Inertia |  | Kg-m2